B USER MANUAL

HYBRID INVERTER

3.6KW/4.2KW/6.2KW

VERSION: 1.0

Table Of Contents

1 ABOUT THIS MANUAL 3

1.1 PURPOSE.......cscsscsssssssscstcssescssssssssesscssestsscesnssssoessssausenscesessnessesneseserssssansucsseanssuesceaseaeegrsassaesecsessnsneneseeaeeerssseaes 3

1.2 SCOPE

2 SAFETY INSTRUCTIONS 3

3. INTRODUCTION A

3.1 FEATURES........cscsssssssscsscssesseseessescsacssssensecscessenessessceoeasssssansecsseauesesesesceoeeassatsenseeseeateseseneaesoesstsatsecssesnsatsessensoeeA

3.2 BASIC SYSTEM ARCHITECTURE..........scssssssssesseccsscsssseeseesccseestesesonsncassassesseeaacaasstsaesecenceasseesessecaeeatsersasseeeaseased A

3.3 PRODUCT OVERVIEW......ccsccsscssssescsssesseessessecssesssessessecssessscsuesnsessesssesesessccseanssenseeusessesssensesusesssesseseeeaeeaeeseeensens 5

4 INSTALLATION &

4.1 UNPACKING AND INSPECTION..

4.2 —_ PREPARATION. ........sssessessssssseenessestestessensonecsssneseesseauensestsseensenessesuusnesseasenseatsnseneasssesuesnesseatenssssenssnesssanesnesseasead

4.3, MOUNTING THE UNIT.)........ccccsssssssencesssssnessessconestssscnesnessesnesuessenseseestsseenesacsnesuescesssacsaessssneenseaeonesuestseseansatsneeed 6

4,4 BATTERY CONNECTION ........:sccsssssssessssseseessesessrestesseoesessssseusuessesesssssrsneeeesassnssuesueseeorssssarsneseessssutsuessesesanssteanses 6

45 AC INPUT/OUTPUT CONNECTION......cccsssscesssssscsstsssssesocssesseseesssscscessssanseeseeseaatssesscsoesaesassassecsnesusaesensoneoeearsassen 8

4.6 > PV CONNECTION.........cccsssssssesccscessessscesecsseseesesseesaesesseeseseesesaaeaeesesseeaccasssseaeseesacaaesessseseeaseassseseeseesacaassesseeseeas 9

4.7 FINAL ASSEMBLY.......c:ccsccssccssssscesesseessesssseseseecssessseesesssecssesssensesuecssesssessesuecssesseesuesssccseaseeensenssessasssesseeusesaeses 11

4.8 COMMUNICATION CONNECTION.......ccsssssssessessestsscensenessessesnessenseseesssoesnessssnesueenssceatenssssensenssssaeessesseosensesesseens 11

5 OPERATION 11

5.1 POWER ON/OFF. .......:ccsseccssssssereesensessestessenssacsnssusonesseacensesssscenscsessesusonesseacensestesseneensssesnesnesneaeeseeenessenseassntenes 11

5.2 OPERATION AND DISPLAY PANEL........csscsssssscsssessssecesseorscsnccacessessessasessesseeonssasesceeeenssnsesaceaesssesenesaqesarsnnseneesees 11

5.3 LCD DISPLAY ICONS. we

5.4 —-_ LCD SETTING... cessssscsscssessssccetsscsccsassansecsncceatesesssssesoessssatsecsccssaasusessneseenesassansecenesuaasesessneseeaesateatseeseesasaes

5.5 DISPLAY SETTING..........csssssssccssessesssesnccscsatseeseesecscestesseesencsassaeseesseaaeaeseeeseseesacsassaeseesceaceatsseeaseueacsatseeseesaeaes

5.6 OPERATING MODE DESCRIPTION .

5.7 BATTERY EQUALIZATION DESCRIPTION.......sscessessssstestsesteeneestesstcensensesssestennsentcentestseteensentesteeeneenessncenseentenes 26

5.8 FAULT REFERENCE CODE......ccsssssssscssssssstessenssasssssnsenessessetestessenesacsnssaeenesseaneasseseresenssesaseneessaenestssseneenesasenss 27

5.9 "WARNING INDICATOR......cccscsscsssssessessesessrsstenssceseesnessesuesseneserssssonseesessnesueoueseserssssausecsaesnssueseeseeaeearsatsneseessesneen 28

6 CLEARANCE AND MAINTENANCE FOR ANTI-DUST KIT 29

6.1 OVERVIEW......cssssssssescsstsstsccsccssesststeesessscesstssesecsnssesstsssesseoesassausecsnesueassatsecensencssssutsacecescensssteaceaeseesatseneaesnesees 29

6.2 | CLEARANCE AND MAINTENANCE .......cscsssssssscssescesteessocsocssssatseeseeseuscestssssoesacsssasseeseeaeeaessessesoesasenssansenseeanenes 29

7 SPECIFICATIONS 30

TABLE 1 LINE MODE SPECIFICATIONG.........s:s:scccsssssssssssssesssesesesessssssssssesesescsssessserecsssessstseseeeseseesesssestessesesaususesrenecesses 31

TABLE 2 INVERTER MODE SPECIFICATIONS... 32

TABLE 3 CHARGE MODE SPECIFICATIONS.........cccsssssssescocssnssscesessecestsssscseesesensssesacseeceassasstsesseseasssessesssceseeassteasseeeeeeas 33

TABLE 4 Grid-Tie Operation ......-.ssecsssessesssssssssssssssessesenssssscesessessusssscesssntssnssessecassuseeseseesessisssscesseatsateassens 33

TABLE 5 GENERAL SPECIFICATIONS........ccccsssscscscsssssssserccsssesssessessessecssessesesesacssessessecsacaesesssseacsssesaeseeecacsaesteesaeseeesense 33,

8 TROUBLE SHOOTING. 33

9 APPENDIX: APPROXIMATE BACK-UP TIME TABLE 34

2

1 ABOUT THIS MANUAL

1.1 Purpose

This manual describes the assembly, installation, operation and troubleshooting of this unit. Please read

this manual carefully before installations and operations. Keep this manual for future reference.

1.2 Scope

This manual provides safety and installation guidelines as well as information on tools and wiring.

2 SAFETY INSTRUCTIONS

WARNING: This chapter contains important safety and operating instructions. Read and

keep this manual for future reference.

1. Before using the unit, read all instructions and cautionary markings on the unit, the batteries and all

appropriate sections of this manual.

2. CAUTION --To reduce risk of injury, charge only deep-cycle lead acid type rechargeable batteries.

Other types of batteries may burst, causing personal injury and damage.

3. Do not disassemble the unit. Take it to a qualified service center when service or repair is required.

Incorrect re-assembly may result in a risk of electric shock or fire.

4. Toreduce risk of electric shock, disconnect all wirings before attempting any maintenance or cleaning.

Turning off the unit will not reduce this risk.

5. CAUTION -— Only qualified personnel can install this device with battery.

NEVER charge a frozen battery.

7. For optimum operation of this inverter/charger, please follow required spec to select appropriate cable

size. It’s very important to correctly operate this inverter/charger.

8. Be very cautious when working with metal tools on or around batteries. A potential risk exists to drop a

tool to spark or short circuit batteries or other electrical parts and could cause an explosion.

9. Please strictly follow installation procedure when you want to disconnect AC or DC terminals. Please

refer to INSTALLATION section of this manual for the details.

10. One piece of 150A fuse is provided as over-current protection for the battery supply.

11. GROUNDING INSTRUCTIONS -This inverter/charger should be connected to a permanent grounded

wiring system. Be sure to comply with local requirements and regulation to install this inverter.

12. NEVER cause AC output and DC input short circuited. Do NOT connect to the mains when DC input

short circuits.

13. Warning! Only qualified service persons are able to service this device. If errors still persist after

following troubleshooting table, please send this inverter/charger back to local dealer or service center

for maintenance.

3 INTRODUCTION

This is a multi-function inverter/charger, combining functions of inverter, solar charger and battery charger to

offer uninterruptible power support with portable size. Its comprehensive LCD display offers user-configurable

and easy-accessible button operation such as battery charging current, AC/solar charger priority, and

acceptable input voltage based on different applications.

3.1 Features

Pure sine wave inverter

Configurable input voltage range for home appliances and personal computers via LCD setting

Configurable battery charging current based on applications via LCD setting

Configurable AC/Solar Charger priority via LCD setting

Compatible to mains voltage or generator power

Auto restart while AC is recovering

Overload/ Over temperature/ short circuit protection

Smart battery charger design for optimized battery performance

Cold start function

DHORAARARADA

3.2 Basic System Architecture

The following illustration shows basic application for this inverter/charger. It also includes following devices to

have a complete running system:

Generator or Utility.

PV modules

Consult with your system integrator for other possible system architectures depending on your requirements.

This inverter can power all kinds of appliances in home or office environment, including motor-type appliances

such as tube light, fan, refrigerator and air conditioner.

Ll

x x

e ~

|

Solar power

= aD

OR

External Home Appliances

Battery packs

Figure 1 Hybrid Power System

3.3 Product Overview

ee

LCD display

Status indicator

Charging indicator

Fault indicator

Function buttons

Power on/off switch

AC input

Main output

Second output

10. Battery input

11. PV input

12. Anti dust kit

13. RS-232 communication port /WiFi-port

CMAN OAunAWN PE

4 INSTALLATION

4.1 Unpacking and Inspection

Before installation, please inspect the unit. Be sure that nothing inside the package is damaged. You should

have received the following items inside of package:

W The unit x 1

User manual x 1

4.2 Preparation

Before connecting all wirings, please take off bottom cover by removing two screws as shown below.

4.3 Mounting the Unit

Consider the following points before selecting where to install:

3 Do not mount the inverter on flammable construction materials.

3 Mount on a solid surface

36 —_ Install this inverter at eye level in order to allow the LCD display to be

read at all times.

38 For proper air circulation to dissipate heat, allow a clearance of approx.

20 cm to the side and approx. 50 cm above and below the unit.

38 The ambient temperature should be between 0°C and 55°C to ensure

optimal operation.

$8 The recommended installation position is to be adhered to the wall

vertically.

#6 Be sure to keep other objects and surfaces as shown in the diagram to

guarantee sufficient heat dissipation and to have enough space for

removing wires.

sy SUITABLE FOR MOUNTING ON CONCRETE OR OTHER NON-COMBUSTIBLE SURFACE ONLY.

Install the unit by screwing two screws. It’s recommended to use M6 screws.

4.4 Battery Connection

CAUTION: For safety operation and regulation compliance, it’s requested to install a separate DC over-current

protector or disconnect device between battery and inverter. It may not be requested to have a disconnect

device in some applications, however, it’s still requested to have over-current protection installed. Please refer

to typical amperage in below table as required fuse or breaker size.

WARNING! All wiring must be performed by a qualified personnel.

WARNING! It's very important for system safety and efficient operation to use appropriate cable for battery

connection. To reduce risk of injury, please use the proper recommended cable as below.

Recommended battery cable size:

Model Wire Size Cable (mm’) Torque value (max)

3.6KW/4.2KW/6.2KW| 1x 2AWG 25 2Nm

Please follow below steps to implement battery connection:

1. Remove insulation sleeve 18 mm for positive and negative conductors.

2. Suggest to put bootlace ferrules on the end of positive and negative wires

with a proper crimping tool.

to

= Ca

3. Connect all battery packs as below chart.

Inverter 3.6 KW/4.2KW

@©

ps __—____

© wy - A ©

Inverter 6. 2KW

Ov LP aw PULP mw PLY ww °

4. Insert the battery wires flatly into battery connectors of inverter and make sure the bolts are tightened with

torque of 2 Nm in clockwise direction. Make sure polarity at both the battery and the inverter/charge is

correctly connected and conductors are tightly screwed into the battery terminals.

Recommended tool: #2 Pozi Screwdriver

\

\

OS 7B -GaSaSo

Say

ie!

.

el

a

oy

i}

ON

]

Sis

i

Sel

\e.

fan

vi

ORO EO

os

&

WARNING: Shock Hazard

Installation must be performed with care due to high battery voltage in series.

CAUTION!!! Before making the final DC connection or closing DC breaker/disconnector, be sure

positive (+) must be connected to positive (+) and negative (-) must be connected to negative

©).

E> || >

4.5 AC Input/Output Connection

CAUTION!!! Before connecting to AC input power source, please install a separate AC breaker between

inverter and AC input power source. This will ensure the inverter can be securely disconnected during

maintenance and fully protected from over current of AC input. The recommended spec of AC breaker is 32A for

3.6KW/4.2KW and 50A for 6.2KW.

CAUTION!!! There are two terminal blocks with “IN” and “OUT” markings. Please do NOT mis-connect input

and output connectors.

WARNING! All wiring must be performed by a qualified personnel.

WARNING! It's very important for system safety and efficient operation to use appropriate cable for AC input

connection. To reduce risk of injury, please use the proper recommended cable size as below.

Suggested cable requirement for AC wires

Model Gauge Cable (mm?) Torque Value

3.6KW/4.2KW 12 AWG 4 1.2 Nm

6.2KW 10 AWG 6 1.2 Nm

Please follow below steps to implement AC input/output connection:

1. Before making AC input/output connection, be sure to open DC protector or disconnector first.

2. Remove insulation sleeve 10mm for six conductors. And shorten phase L and neutral conductor N 3 mm.

3. Insert AC input wires according to polarities indicated on terminal block and tighten the terminal screws.

L—LINE (brown or black)

N—Neutral (blue)

( WARNING:

Be sure that AC power source is disconnected before attempting to hardwire it to the unit.

4. Then, insert AC output wires according to polarities indicated on terminal block and tighten terminal screws.

L—LINE (brown or black)

N—Neutral (blue)

5. Then, insert AC output wires according to polarities indicated on terminal block and tighten terminal screws.

L-LINE (brown or black)

N—Neutral (blue)

6. Make sure the wires are securely connected.

CAUTION: Appliances such as air conditioner are required at least 2~3 minutes to restart because it’s required

to have enough time to balance refrigerant gas inside of circuits. If a power shortage occurs and recovers in a

short time, it will cause damage to your connected appliances. To prevent this kind of damage, please check

manufacturer of air conditioner if it’s equipped with time-delay function before installation. Otherwise, this

inverter/charger will trig overload fault and cut off output to protect your appliance but sometimes it still causes

internal damage to the air conditioner.

4.6 PV Connection

CAUTION: Before connecting to PV modules, please install separately a DC circuit breaker between inverter

and PV modules.

WARNING! It's very important for system safety and efficient operation to use appropriate cable for PV

module connection. To reduce risk of injury, please use the proper recommended cable size as below.

Model Wire Size Cable (mm?) Torque value (max)

3.6KW/4.2KW/6.2KW 1 x 12AWG 4 1.2 Nm

PV Module Selection:

When selecting proper PV modules, please be sure to consider below parameters:

1. Open circuit Voltage (Voc) of PV modules not exceeds max. PV array open circuit voltage of inverter.

2. Open circuit Voltage (Voc) of PV modules should be higher than min. battery voltage.

INVERTER MODEL 3.6KW/4.2KW 6.2KW

Max. PV Array Open Circuit Voltage 500Vdc

PV Array MPPT Voltage Range 60Vdc~450Vdc

Take 250Wp PV module as an example. After considering above two parameters, the recommended module

configurations are listed as below table.

Solar Panel Spec. SOLAR INPUT tty of panels} Ot! input

Site (Min in serial: 6 pcs, max. in serial: 13 pcs) Q'ty of panels power

- Vmp:  o.iVvde 6 pcs in serial 6 pcs 1500W

- Imp: 8.3A 8 pcs in serial 8 pcs 2000W

- Voc: 37.Wdc 12 pcs in serial 12 pcs 3000W

- Isc: 8.4A 13 pcs in serial 13 pes 3250W

- Cells: 60 8 pieces in serial and 2 sets in parallel 16 pcs 4000W

10 pieces in serial and 2 sets in parallel 20 pcs 5000W

10 pieces in serial and 2 sets in parallel 20 pcs 6200W

12 pieces in serial and 2 sets in parallel 24 pcs 6500W

10 pieces in serial and 3 sets in parallel 30 pcs 7500W

PV Module Wire Connection

Please follow below steps to implement PV module connection: _—— +

1. Remove insulation sleeve 10 mm for positive and negative conductors.

2. Suggest to put bootlace ferrules on the end of positive and negative wires with a _

proper crimping tool.

3. Check correct polarity of wire connection from PV modules and PV input connectors. Then, connect positive

pole (+) of connection wire to positive pole (+) of PV input connector. Connect negative pole (-) of

connection wire to negative pole (-) of PV input connector.

Recommended tool: 4mm blade screwdriver

e

®

oc]

=)

ag

ay

ORO

Sp

oy

ORD

AD

O@

15)

c=

e,

<C>

so)

Si

‘e)

a

‘e)

@

les)

eRe

ORR

ecen

one

Sena

ERO

ERG

eet

ene te

Seo

a

oe)

ERO)

Sey

a

ie

OSE

va!

Ge

Se

SO

4.7 Final Assembly

After connecting all wirings, please put bottom cover back by screwing two screws as shown below.

4.8 Communication Connection

1. Wi-Fi cloud communication (option):

Please use supplied communication cable to connect to inverter and Wi-Fi module. Download APP and installed

from APP store, and Refer to “Wi-Fi Plug Quick Installation Guideline” to set up network and registering. The

inverter status would be shown by mobile phone APP or webpage of computer.

10

2. GPRS cloud communication (option):

Please use supplied communication cable to connect to inverter and GPRS module, and then applied external

power to GPRS module. Download APP and installed from APP store, and Refer to “GPRS RTU Quick Installation

Guideline” to set up network and registering. The inverter status would be shown by mobile phone APP or

webpage of computer.

WIFI

RGB Light (option )

@) Battery Mode:red Light

@) Utility Mode:blue Light

@) PV Mode:purple Light

5 OPERATION

5.1 Power ON/OFF

Side view of unit

al

ea

Once the unit has been properly installed and the batteries are connected well, simply press On/Off switch

(located on the button of the case) to turn on the unit.

5.2 Operation and Display Panel

The operation and display panel, shown in below chart, is on the front panel of the inverter. It includes three

indicators, four function keys and a LCD display, indicating the operating status and input/output power

information.

11

0000

Function keys

LCD display

LED Indicator

LED Indicator Messages

Solid On | Output is powered by utility in Line mode.

INV/AC & Green ; ; :

Flashing | Output is powered by battery or PV in battery mode.

Solid On /Battery is fully charged.

CHG & Green - ry - y : g

Flashing /|Battery is charging.

Solid On | Fault occurs in the inverter.

FAULT & Red - - ; ;

Flashing | Warning condition occurs in the inverter.

Function Keys

Function Key | Description

ESC To exit setting mode

UP To go to previous selection

DOWN To go to next selection

ENTER To confirm the selection in setting mode or enter setting mode

5.3. LCD Display Icons

Icon

Function description

Input Source Information

Indicates the AC input.

Indicates the PV input

Indicate input voltage, input frequency, PV voltage, charger current (if PV in

charging for 3.6KW models), charger power, battery voltage.

12

Configuration Program and Fault Information

A

088

Indicates the setting programs.

gag2

Indicates the warning and fault codes.

Warning: 888 2 flashing with warning code.

Fault: 888 & lighting with fault code

Output Information

boo*

Indicate output voltage, output frequency, load percent, load in VA, load in

Watt and discharging current.

Battery Information

sh,

Load Information

OVER LOAD

Bs

Indicates overload.

Mode Operation Information

Indicates unit connects to the mains.

bey

Indicates unit connects to the PV panel.

AC BYPASS

Indicates load is supplied by utility power.

Indicates the utility charger circuit is working.

Indicates the DC/AC inverter circuit is working.

Mute Operation

che

Indicates unit alarm is disabled.

13

5.4 LCD Setting

After pressing and holding ENTER button for 3 seconds, the unit will enter setting mode. Press “UP” or “DOWN”

button to select setting programs. And then, press “ENTER” button to confirm the selection or ESC button to

exit.

Setting Programs:

Program Description

Selectable option

00 Exit setting mode

Escape (default)

on

uu GOE

One-button restore setting options

nn

uu GUA

Output source priority:

01 Toconfigure load power

source priority

Utility first

nt -

ui! Uo

Utility will provide power to the

loads as first priority.

Solar and battery energy will

provide power to the loads only

when utility power is not available.

Solar first (default)

Gi Su

Solar energy provides power to

the loads as first priority.

If solar energy is not sufficient to

power all connected loads, utility

will supply power to the loads at

the same time.

Battery provides power to the

loads only when any one condition

happens:

- Solar energy and utility is not

available.

- Solar energy is not sufficient and

utility is not available.

SBU priority

Ut Shu

Solar energy provides power to

the loads as first priority.

If solar energy is not sufficient to

power all connected loads, battery

energy will supply power to the

loads at the same time.

Utility provides power to the loads

only when battery voltage drops

to either low-level warning voltage

or the setting point in program 12.

02 chargers.

solar charging current)

Maximum charging current:

To configure total charging

current for solar and utility

(Max. charging current =

utility charging current +

10A 20A 30A

Uc 0: Ge 20:0e 30:

40A 50A 60A (default)

Uc 4p: Ge so-Ge 60:

14

70A 80A 90A

m = mn nm Bini

Uc Ie Uc ane an

100A 110A 120A

Imma, m bimalA ! a

Uc Muu Uc ane Uc ICU

Q@ ———— @ @

Appliances (default) If selected, acceptable AC input

{| 5 O 0 1 voltage range will be within

AC input voltage range 20°280VAC.

P 9 9 UPS If selected, acceptable AC input

m2 voltage range will be within

Wo

i IP3 170-280VAC.

AGM (default) Flooded

Mm rm mM '

i) G O unm | 5 Cr L ra

| User-Defined If “User-Defined” is selected,

Battery type n C ‘I battery charge voltage and low DC

W Ul 5 E cut-off voltage can be set up in

— program 26, 27 and 29.

User-Defined When the solar energy exists, Set this

HS oe item to LIB, and the lithiumbattery

LIO will be activated for 3 second.

User-Defined If selected, Lithium battery communicotion

Qj tar connection for PACE BMS.

7) Lik

Aut tart wh load Restart disable (default) Restart enable

uto restart when overloa =

mM mM

occurs U b WJ o L F E

Auto restart when over Restart disable (default) Restart enable

temperature occurs | a4

I

OT kd G7 EEE

50Hz (default) 60Hz

Output frequency n ri

US 50. US 60.

a roll (default)

! 357 My

WJ 1

Output voltage ecu cu" IU

240V

m4

WwW c UY iy

Maximum utility charging | 2A 10A

1 | — =

current i | 2 | ' | ! n O

Note: If setting value in

program 02 is smaller than | 20A 30A (default)

that in program in 11, the oe ies | | mo

inverter will apply charging At cu H 1 SUA wr

current from program 02 for | 404 50A

utility charger. tt 4

11 4A 11 SUA

60A 70A 80A

1d 1} It

't BUA i OR |. BUR

a (2) 2)

90A ae

1 1 !

11 SOA 114007

Available options in 3.6KW/4.2KW model:

21.0V 21.5V 22.0V

\ BATT | BATT \ 35 ci

1 21 le 21s ais: 1 Phy

22.5V 23.0V (default) 23.5V

Cc —_ BATT BATT

| | 7754 ! 7

Ie ees jie 230' fie 235:

24.0V 24.5V

| uA ac

ic eu . ic cus :

25.0V 25.5V

Setting voltage point back

to utility source when

BATT

2250

BATT

Ie 25S"

12 a Ww H 7 a

selecting SBU priority” or | Available options in 6.2KW model:

Solar first” in program 01. 42V 43V 44V

\ > BATT - \ > BATT | > BATT

ic Uy ic Uy IC Lily

45V 46V (default) 47V

BATT BATT _ BATT

| IT — 1)

ie 4S ic Brie

48V 49vV

BATT -_ BATT

I 1

ic 4B ic 4

50V 51V

BATT -_, BATT

17) [~ !

2 So | te Sh

13 Setting voltage point back | Available options in 3.6KW/4.2KW model:

16

to battery mode when

selecting “SBU priority” or

“Solar first” in program 01.

Battery fully charged 24V

I 7 _ BATT \ 7 BATT

IJ FUL | 2up

24.5V 25V

i 7 BATT ! -, BATT nm

3 P4S jis 250

25.5V 26V

\ BATT ' | BATT

3 26S [13 eb

26.5V 27V (default)

' 7 Cc _ | | BATT an

Oo cbs to oe Ww

27.5V 28V

| 7 BATT , t 7 a4 ;

I PS to CBU

28.5V 29V

7 BATT 4 BATT

3 CAS js 29th

Available options in 6.2KW model:

Battery fully charged 48V

- BATT — BATT

IS FUL id YD

49V 50V

"i BATT 7 BATT

in YON IF ont

51V 52V

\ a BATT \ | BATT

3 Sib fia Se

53V 54V (default)

-, BATT -, BATT

! Lo mM v | _ m Vv

is S3u is S44

17

55V 56V

| 7 BATT \ 7 __ BATT

I oof . Ia U ”

57V 58V

| - a \ - BATT 7

- [_ v _ CaM,

io SU i 30

Charger source priority:

If this inverter/charger is working in Line, Standby or Fault mode,

charger source can be programmed as below:

Solar first

!

1D to ie CSU

Solar energy will charge battery as

first priority.

Utility will charge battery only

when solar energy is not available.

Solar and Utility (default)

Solar energy and utility will charge

16 To configure charger ! tC crit battery at the same time.

source priority I tu

Only Solar Solar energy will be the only

tm acon charger source no matter utility is

UU available or not.

If this inverter/charger is working in Battery mode or Power saving

mode, only solar energy can charge battery. Solar energy will

charge battery if it's available and sufficient.

Alarm on (default) Alarm off

18 Alarm control ! om I rm

18 bon id bOF_

Return to default display If selected, no matter how users

screen (default) switch display screen, it will

1C LCEeEa automatically return to default

Cor display screen (Input voltage

19 Auto return to default /output voltage) after no button is

display screen ‘

pressed for 1 minute.

Stay at latest screen If selected, the display screen will

iC) _tloa stay at latest screen user finally

tt switches.

Backlight on (default) ane off

20 Backlight control monn !

9 cu Lon PU LUFF

18

Beeps while primary source

Alarm on (default) Alarm off

|

22 is interrupted 2 2 a AUT M - Cc O f} Cr

Overload bypass: Bypass disable (default) Bypass enable

When enabled, the unit will

23 transfer to line mode if 2 = _—

P | _I_l

overload occurs in battery a L, U Oo cu Ly L, | | t

Record enable (default) Record disable

25 Record Fault code ecm C coc

co FEA fed FAS

3.6KW/4.2KW default setting: 28.2V

_ 25 an

6.2KW default setting: 56.4V

6 Bulk charging voltage _

(C.V voltage) | -

[ LI oe Aaa = —Sbu" he Iv

If self-defined is selected in program 5, this program can be set

up. Setting range is from 25.0V to 29.0V for 3.6KW/4.2KW model

and 48.0V to 58.0V for 6.2KW model. Increment of each click is 0.1V.

3.6KW/4.2KW default setting: 27.0V

c - - =" |

iu - Wy

re & !o cw

6.2KW default setting: 54.0V

27 Floating charging voltage FLY 23 sda: ‘on

a i) al ly

If self-defined is selected in program 5, this program can be set

up. Setting range is from 25.0V to 29.0V for 3.6KW/4.2KW model

and 48.0V to 58.0V for 6.2KW model. Increment of each click is 0.1V.

3.6KW/4.2KW default setting: 20.0V

> rm BATT 7

Cow ef eu Woy

LuU- © cuu

29 Low DC cut-off voltage

6.2KW default setting: 40.0V

BATT

rau e3 400" ur rity

19

If self-defined is selected in program 5, this program can be set

up. Setting range is from 20.0V to 24.0V for 3.6KW/4.2KW model

and 40.0V to 48.0V for 6.2KwW model. Increment of each click

is 0.1V. Low DC cut-off voltage will be fixed to setting value no

matter what percentage of load is connected.

Battery equalization Battery equalization disable (default)

JQ con 44 cac

St Ju

30 Battery equalization Ctl _to3_

If “Flooded” or “User-Defined” is selected in program 05, this

program can be set up.

3.6KW/4.2KW default setting: 29.2V

cu J! 300

Cu - |

Cc (a Cc IC "

a 6.2KW default setting: 58.4V

31 Battery equalization voltage 7 BATT

Tu - I

EY at SAY

Setting range is from 25.0V to 31.5V for 3.6KW/4.2KW model and

48.0V to 61.0V for 6.2Kw model. Increment of each click is 0.1V.

60min (default) Setting range is from 5min to 900min.

33 Battery equalized time 4 _ C mn Increment of each click is 5min.

ae UW

120min (default) Setting range is from Smin to 900 min.

34 Battery equalized timeout 44 mn Increment of each click is 5 min.

IL

30days (default) Setting range is from 0 to 90 days.

35 Equalization interval 4 G 4 rm Increment of each click is 1 day

= Ju

Enable Disable (default)

ocn IC

4 b | Mcit Lil 5 6 H d I

— ; If equalization function is enabled in program 30, this program can

36 Equalization activated be set up. If “Enable” is selected in this program, it’s to activate

immediately battery equalization immediately and LCD main page will shows

“C1”, If “Disable” is selected, it will cancel equalization function

until next activated equalization time arrives based on program 35

-

setting. At this time, “EG. will not be shown in LCD main page.

Off grid (default) Inverter operates only in off-grid

5 7 mode. Solar energy provides power to

tl F i. the loadsas first priority and charging

; ; second

37 GRID-tie operation

Hybrid Inverter operates hybrid mode. Solar

energy provides power to the loads as

first’ priorityand charging second

Excess energy feed to grid.

37 Yd

20

38 GRID-tie current 35 | 0 A Increment of each click is 2A.

Led pattern off Led pattern on(default)

39 Led pattern light 49 | OF 39 (on

disable (default) use

41 Dual output al | OF al { 20

3.6KW/4.2KW default setting: 22.0V

42 220

42 Enter the dual output 6.2KW default setting: 44.0V

functional voltage point

42 440

Setting range is from 20.0V to 23.0V for 24VDC model and 40.0V

to 46.0V for 48VDC model. Increment of each click is 0.1V.

5.5 Display Setting

The LCD display information will be switched in turns by pressing “UP” or “DOWN” key. The selectable

information is switched as below order: input voltage, input frequency, PV voltage, charging current, charging

power, battery voltage, output voltage, output frequency, load percentage, load in Watt, load in VA, load in Watt,

DC discharging current, main CPU Version.

Selectable information | LCD display

Charged state, and the power is less than 1kw

Input voltage=222V , cece” cece’ 198 .

PV voltage=168V, xy : Lene

Battery voltage=25V, ———— a

Output voltage=222V, 1 5

Load in Watt=188W, —l =. nme a

Chg(Flashing), Inv/ac(bright) 68 eS

ia ore ees" ech (99«

current=2.3A, a

Battery current=20A, 4 come - | &

Output voltage=224V, | ; =

Load in VA=188VA, tA— mo. oot

Chg(Flashing), Inv/ac(bright) es: ei.

Input voltage=223V , ecs' 450. 12.

Pv ntc temperture=71.0°C, at

Battery voltage=25V, RE mn ~ i - » og

Inv ntc temperture=35.0°C, } + =

Load percentage=12%, {4  . -

Chg(Flashing), Inv/ac(bright) q 1H. Pa .

21

Input frequency=50.0Hz ,

PV power=0.434KWh,

Battery current=20A,

Output frequency=50.0Hz,

Load in watt=188W,

Chg(Flashing), Inv/ac(bright)

4.

GH3u"

om ..

eu.

Charged state, and the power is greater than 1kw

Input voltage=222V ,

PV voltage=168V,

Battery voltage=25V,

Output voltage=222V,

Load in Watt=1.18KW,

Chg(Flashing), Inv/ac(bright)

Input voltage=224V ,

PV current=8.6A,

Battery current=12.5A,

Output voltage=222V,

Load in VA=1.88KVA,

Chg(Flashing), Inv/ac(bright)

Input voltage=223V ,

Pv ntc temperture=71.0°C,

Battery voltage=25V,

Inv ntc temperture=35.0°C,

Load percentage=82%,

Chg(Flashing), Inv/ac(bright)

Input frequency=50.0Hz,

PV power=1.434KWh,

Battery current=20A,

Output frequency=50.0Hz,

Load in watt=1.88KW,

Chg(Flashing), Inv/ac(bright)

eum

cue IS [oy

meet co un

22

Discharged state, and the power is less than 1kw

¥ Ww

Input voltage=0V , th cece Hate

PV voltage=0V,

Battery voltage=25V, | - |

Output voltage=222V, i =

Load in Watt=188W, im .. wa a

Chg(turn off), Inv/ac(Flashing) ny 2s"

¥

Input voltage=OV , ty eee 198"

PV current=0A, a

Battery current=12.5A, | - I

Output voltage=222V, }

Load in VA=188VA, fH. wt

Chg(turn off), Inv/ac(Flashing) Oj. H ce A

Input voltage=0V , Hie 468. 13.

Pv ntc temperture=60.0°C,

Battery voltage=24V, =| _— bore &

Inv ntc temperture=36.0°C, i =

Load percentage=13%, = comme &

Chg(turn off), Inv/ac(Flashing) 600. c4

Input frequency=0Hz, He S0G.- 190"

PV power=OKWh,

Battery current=12A, a |

Output frequency=50.0Hz, =

Load in watt=188W, = on 8

Chg(turn off), Inv/ac(Flashing) ang a i>

h ic*

23

Discharged state, and the power is greater than 1kw

Input voltage=OV ,

PV voltage=0V,

Battery voltage=25V,

Output voltage=222V,

Load in Watt=1.88KW,

Chg(turn off), Inv/ac(Flashing)

Oy eee’

H

i .. INvAc &

oo”

LI

Input voltage=OV ,

PV current=0A,

Battery current=111A,

Output voltage=222V,

Load in VA=1.88KVA, es

Chg(turn off), Inv/ac(Flashing) m it

Lj* be

= Mv nn '

Input voltage=OV , Ht 308. 6 te

Pv ntc temperture=68.0°C,

Battery voltage=24V, =| eeneeees oe Rs)

Inv ntc temperture=30.0°C, ; =

Load percentage=81%, = wc h

Chg(turn off), Inv/ac(Flashing)

rs

680. cy

Input frequency=0Hz ,

PV power=0KWh,

Battery current=111A,

Output frequency=50.0Hz,

Load in watt=1.21KW,

Chg(turn off), Inv/ac(Flashing)

O- SU0-

Gogo” th

Main CPU version checking

Main CPU version 24 00

24

5.6 Operating Mode Description

Operation mode

Selectable information

LCD display

Stanby mode

Input voltage=222V ,

PV voltage=210V,

Battery voltage=25V,

Output voltage=0V,

Load in Watt=0W,

Chg(Flashing), Inv/ac(bright)

Input voltage=223V ,

PV voltage=0V,

Battery voltage=25V,

Output voltage=0V,

Load in Watt=0W,

Chg(Flashing), Inv/ac(bright)

Input voltage=0V ,

PV voltage=210V,

Battery voltage=25V,

Output voltage=0V,

Load in Watt=0W,

Chg(Flashing)

Line mode

Input voltage=224V ,

PV current=8.6A,

Battery current=12.5A,

Output voltage=222V,

Load in VA=1.88KVA,

Chg(Flashing), Inv/ac(bright)

Input voltage=224V ,

PV voltage=0V,

Battery voltage=25V,

Output voltage=222V,

Load in Watt=188W,

Chg(Flashing), Inv/ac(bright)

2a eee 108"

3" meapeenne

Grid-Tie Operation

Input voltage=224V ,

PV current=8.6A,

Battery current=12.5A,

Output voltage=222V,

Load in VA=1.88KVA,

Chg(Flashing), Inv/ac(bright)

When working in Grid-Tie mode, the #2

will be flash 3S/times.

25

Operation mode

Selectable information

LCD display

Input voltage=OV ,

PV voltage=180V,

Battery voltage=25V,

Output voltage=230V,

Load in Watt=388W,

Inv/ac(Flashing)

Battery mode

388 *

Gy 230"

_—<

i B-

Input voltage=0V ,

PV voltage=180V,

Battery voltage=25V,

Output voltage=230V,

G’ 230° 388°

4 n rs

Load in Watt=388wW, : tT ou

Chg(Flashing), Inv/ac(Flashing) id! Mk

80° 2S

Selectable information LCD display

LIC(Lithium battery commun

ication connection)

Total battery voltage=52.4V

Battery residual capacity=23%

Sc" oJ:

Total battery capacity=100AH

= mveac &

Mm fa

Battery charging current=0A al

Battery discharge current=1A B eee Prvereens a

Yon. mn

Ly ee

Nominal battery voltage=48V

Battery remaining capacity=23%

Battery charger/discharge Times =8

26

sattervambiemttemperetureeprc] TOD esg

attery ambient temperature=28.2°

Battery MOS temperature=28.9°C = sete Dreneonn a

3c c85

Single battery voltage=3.27V

Single battery temperature=28.5°C =| — =n &

5.7 Battery Equalization Description

Equalization function is added into charge controller. It reverses the buildup of negative chemical effects like

stratification, a condition where acid concentration is greater at the bottom of the battery than at the top.

Equalization also helps to remove sulfate crystals that might have built up on the plates. If left unchecked, this

condition, called sulfation, will reduce the overall capacity of the battery. Therefore, it’s recommended to

equalize battery periodically.

38 How to Apply Equalization Function

You must enable battery equalization function in monitoring LCD setting program 30 first. Then, you may apply

this function in device by either one of following methods:

1. Setting equalization interval in program 35.

2. Active equalization immediately in program 36.

36 When to Equalize

In float stage, when the setting equalization interval (battery equalization cycle) is arrived, or equalization is

active immediately, the controller will start to enter Equalize stage.

A

Equalize Voltage

Float Voltage

ULK ABSORPTION FLOAT EQUALIZE FLOAT

27

3 Equalize charging time and timeout

In Equalize stage, the controller will supply power to charge battery as much as possible until battery voltage

raises to battery equalization voltage. Then, constant-voltage regulation is applied to maintain battery voltage

at the battery equalization voltage. The battery will remain in the Equalize stage until setting battery equalized

time is arrived.

A

Equalize

Charging Time

Equalize Voltage |—- — — Lees

Absorption Voltage |-—

Float Voltage F- LK ABSORPT. FLOAT 4]

~ EQUALIZE —

=

However, in Equalize stage, when battery equalized time is expired and battery voltage doesn’t rise to battery

equalization voltage point, the charge controller will extend the battery equalized time until battery voltage

achieves battery equalization voltage. If battery voltage is still lower than battery equalization voltage when

battery equalized timeout setting is over, the charge controller will stop equalization and return to float stage.

A

Equalize Charging

Timeout

Equalize Voltage EE

a — — — — eat

Absorption Voltage |-—— 7 |

Float Voltage [-——~— ABSORPT, l__ =

a EQUALIZE

—

5.8 Fault Reference Code

Fault Code Fault Event Icon on

01 Fan is locked when inverter is off. Hh ERROR

02 Over temperature U C ERROR

03 Battery voltage is too high U =| ERROR

04 Battery voltage is too low u ee

05 Output short circuited or over temperature is detected by | m S

internal converter components. US error

06 Output voltage is too high. Hi I ERROR

07 Overload time out 07 ERROR

08 Bus voltage is too high 08 ERROR

09 Bus soft start failed U Gg ERROR

51 Over current or surge G | ERROR

28

52 Bus voltage is too low Se ERROR

53 Inverter soft start failed G = ERROR

55 Over DC voltage in AC output 55 ERROR

57 Current sensor failed | ERROR

58 Output voltage is too low SA ERROR

59 PV voltage is over limitation OG on

5.9 Warning Indicator

wee Warning Event Audible Alarm Icon flashing

01 Fan is locked when inverter | Beep three times every nN le

is on. second ul

' _ A @

03 Battery is over-charged Beep once every second u 4

04 Low battery Beep once every second Ye

07 Overload Beep once every 0.5 second 0 7 @

10 Output power derating Beep twice every 3 seconds Ht @

15 PV energy is low. Beep twice every 3 seconds 1G @

é4 Battery equalization None Eq ©

()

b p Battery is not connected None b p

29

6 CLEARANCE AND MAINTENANCE FOR ANTI-DUST KIT

6.1 Overview

Every inverter is already installed with anti-dusk kit from factory. Inverter will automatically detect this kit and

activate internal thermal sensor to adjust internal temperature. This kit also keeps dusk from your inverter and

increases product reliability in harsh environment.

6.2 Clearance and Maintenance

Step 1: Please loosen the screw in counterclockwise direction on the top of the inverter.

®

fo oe)

0)

|

eeece

—

Step 2: Then, dustproof case can be removed and take out air filter foam as shown in below chart.

a=) So

|

OOOO

—

Step 3: Clean air filter foam and dustproof case. After clearance, re-assemble the dust-kit back to the inverter.

NOTICE: The anti-dust kit should be cleaned from dust every one month.

30

7 SPECIFICATIONS

Table 1 Line Mode Specifications

INVERTER MODEL 3.6KW 4.2KW 6.2KW

Input Voltage Waveform Sinusoidal (utility or generator)

Nominal Input Voltage 230Vac

170Vac+7V (UPS);

Low Loss Voltage

9 90Vac+7V (Appliances)

180Vac+7V (UPS);

Low Loss Return Voltage

100Vac+7V (Appliances)

High Loss Voltage 280Vac+7V

High Loss Return Voltage 270Vact7V

Max AC Input Voltage 300Vac

Nominal Input Frequency

50Hz / 60Hz (Auto detection)

Low Loss Frequency 40+1Hz

Low Loss Return Frequency 42+1Hz

High Loss Frequency 65+1Hz

High Loss Return Frequency 63+1Hz

Output Short Circuit Protection

Circuit Breaker

Efficiency (Line Mode)

>95% ( Rated R load, battery full charged )

Transfer Time

10ms typical (UPS);

20ms typical (Appliances)

Output power derating:

When AC input voltage drops to 170V,

the output power will be derated.

Output Power

A

Rated Power

50% Power

>»

>

90V 170V 280V Input Voltage

31

Table 2 Inverter Mode Specifications

INVERTER MODEL

3.6KW

4.2KW

6.2KW

Rated Output Power

3.6KW

4.2KW

6.2KW

Output Voltage Waveform Pure Sine Wave

Output Voltage Regulation 230Vact5%

Output Frequency 50Hz

Peak Efficiency 93%

Overload Protection

3s@2>150% load; 5s@101%~150% load

Surge Capacity 2* rated power for 5 seconds

Nominal DC Input Voltage 24Vdc 48Vdc

Cold Start Voltage 23.0Vdc 46.0Vdc

Low DC Warning Voltage

@ load < 50% 22.0Vdc 44.0Vdc

@ load = 50% 21.0Vdc 42.0Vdc

Low DC Warning Return Voltage

@ load < 50% 22.5Vdc 45.0Vdc

@ load = 50% 22.0Vdc 44.0Vdc

Low DC Cut-off Voltage

@ load < 50% 20.5Vdc 41.0Vdc

@ load = 50% 20.0Vdc 40.0Vdc

High DC Recovery Voltage 32Vdc 62Vdc

High DC Cut-off Voltage 33Vdc 63Vdc

No Load Power Consumption 30W 35W 50W

Table 3 Two Load Output Power

INVERTER MODEL 3.6KW 4.2KW 6.2KW

Full Load 3600W 4200W 6200W

Maximum Main Load 3600W 4200W 6200W

Maximum Second Load(battery model) 1200W 1400W 2066W

Main Load Cut Off Voltage 22VDC 44VDC

Main Load Return Voltage 26VDC 52VDC

32

Table 4 Charge Mode Specifications

Utility Charging Mode

INVERTER MODEL 3.6KW 4.2KW 6.2KW

Charging Algorithm 3-Step

AC Charging Current (Max) 100Amp (@Vye=230Vac)

Bulk Charging| Flooded Battery 29.2 58.4

Voltage AGM / Gel Battery 28.2 56.4

Floating Charging Voltage 27Vdc 54Vdc

Battery Voltage, per cell Charging Current, %

“ +p 100%.

Charging Curve som

Time

Bulk Absorption

(Constant Current) (Constant Voltage)

MPPT Solar Charging Mode

INVERTER MODEL 3.6KW 4.2KW 6.2KW

Max. PV Array Power 6200W 6500W

Nominal PV Voltage 240Vdc 360Vdc

PV Array MPPT Voltage Range 60Vdc~450Vdc

Max. PV Array Open Circuit Voltage 500Vdc

Max Charging Current

(AC charger plus solar charger) 120Amp 120Amp 120Amp

Table 5 Grid-Tie Operation

INVERTER MODEL 3.6KW 4.2KW 6.2KW

Nominal Output Voltage 220/230/240 VAC

Feed-in Grid Voltage Range 195 ~253VAC

Feed-in Grid Frequency Range 49~51+ 1Hz/59~6141Hz

Nominal Output Current 15.7A | 182A | 26.9A

Power Factor Range >0.99

Maximum Conversion Efficien

(DC/AC) 97%

Table 6 General Specifications

INVERTER MODEL 3.6KW 4.2KW 6.2KW

Safety Certification CE

Operating Temperature Range -10°C to 50°C

Storage temperature -15°C~ 60°C

Humidity 5% to 95% Relative Humidity (Non-condensing)

Dimension (D*W*H), mm 110X334X423

Net Weight, kg 9 9.5 | 10

33

8 TROUBLE SHOOTING

Problem LCD/LED/ Buzzer Explanation / Possible cause What to do

Unit shuts down LCD/LEDs and buzzer

automatically will be active for 3 The battery voltage is too low 1. Re-charge battery.

during startup seconds and then (<1.91V/Cell) 2. Replace battery.

process. complete off.

No response after 1, The battery voltage is far too ro Necng the fuse ‘or

p No indication. low. (<1.4V/Cell) P g .

power on.

2. Internal fuse tripped.

2. Re-charge battery.

3. Replace battery.

Mains exist but the

unit works in

battery mode.

Input voltage is

displayed as 0 on the

LCD and green LED is

flashing.

Input protector is tripped

Check if AC breaker is tripped

and AC wiring is connected

well.

Green LED is flashing.

Insufficient quality of AC power.

(Shore or Generator)

1. Check if AC wires are too

thin and/or too long.

2. Check if generator (if

applied) is working well or if

input voltage range setting is

correct. (UPS@ Appliance)

Green LED is flashing.

Set “Solar First” as the priority of

output source.

Change output source priority

to Utility first.

When the unit is

turned on, internal

LCD display and LEDs

Battery is disconnected.

Check if battery wires are

relay is switched on | are flashing connected well.

and off repeatedly.

. . Reduce the connected load by

Overload error. The inverter is ee

Fault code 07 5 a switching off some

overload 110% and time is up. equipment.

Check if wiring is connected

Output short circuited. well and remove abnormal

Fault code 05 load.

Temperature of internal converter | Check whether the air flow of

component is over 120°C. the unit is blocked or whether

Internal temperature of inverter the ambient temperature is

Fault code 02 component is over 100°C. too high.

Battery is over-charged. Return to repair center.

Buzzer beeps Fault code 03 Check if spec and quantity of

continuously and The battery voltage is too high. batteries are meet

red LED is on. requirements.

Fault code 01 Fan fault Replace the fan.

Output abnormal (Inverter voltage | 1. Reduce the connected

Fault code 06/58 below than 190Vac or is higher load.

than 260Vac) 2. Return to repair center

Fault code . .

08/09/53/57 Internal components failed. Return to repair center.

Fault code 51

Over current or surge.

Fault code 52

Bus voltage is too low.

Fault code 55

Output voltage is unbalanced.

Restart the unit, if the error

happens again, please return

to repair center.

34

9 Appendix: Approximate Back-up Time Table

Model Load (W) Backup Time @ 24Vdc 100Ah (min) Backup Time @ 24Vdc 200Ah (min)

300 449 1100

600 222 525

900 124 303

1200 95 227

1500 68 164

3.6KW 1800 56 126

4.2KW 2100 48 108

2400 35 94

2700 31 74

3200 28 67

3600 25 60

4200 22 53

Model Load (W) Backup Time @ 48Vdc 100Ah (min) Backup Time @ 48Vdc 200Ah (min)

500 613 1288

1000 268 613

1500 158 402

2000 111 271

6.2KW 2500 90 215

3200 76 182

3500 65 141

4000 50 112

4500 44 100

5000 40 90

6200 36 80

Note:1 .Backup time depends on the quality of the battery, age of battery and type of battery.

Specifications of batteries may vary depending on different manufacturers.

2.The final interpretation right of this product belongs to the company.

35

DZ0-9ZLOOL-2ZE

OY 5 RY Se 2K BET; OE

\ “Bf Ay Ua Ae SY LF tsk

‘WS ds0si M “MAA MES COTIB FE + Hy hy

‘UWOTC#CP TA A Me tT Ke